## Sheet1
Created 12/22/02
UCSC Infill Apartments Project -Cowell
Fiber Optic Loss Test Results
144-strand hybrid cable from ADF3 to 69-2-8, spliced into existing cables in Cowell Residence Bldgs.
Part number: DX-144-155D-96W3eb/1uc/48s.5mc/.5md-FRP
Index of refraction: SM: 1.4580; MM: 1.4830
Dates of Tests: Dec. 21 & 22, 2002
Date of Test: Feb 20, 2003
Operators: Linda RH, Lindy Cloud,Neil Goldstein
Equipment |  | Noyes OLS2-Dual - OPM 5
Calibration Date: 2/2003
|  |  | Loss in decibels | UCSC Test
| Spliced | Total length | Measured at ADF3 | Measured at ADF3
Strd. | to Bldg. | (Meters) | Single Mode 1310nM | Single Mode 1310nM
1 | Prescott | 484 | 0.65 | 0.71
2 | Prescott | 484 | 0.55 | 0.46
3 | Prescott | 484 | 0.75 | 0.61
4 | Prescott | 484 | 0.4 | 0.66
5 | Prescott | 484 | 0.65 | 0.85
6 | Prescott | 484 | 1 | 0.83
7 | Prescott | 484 | 0.5 | 0.61
8 | Prescott | 484 | 0.95 | 0.67
9 | Prescott | 484 | 0.65 | 0.59
10 | Prescott | 484 | 0.95 | 0.62
11 | Prescott | 484 | 0.85 | 0.44
12 | Prescott | 484 | 1.1 | 0.8
13 | Prescott | 484 | 0.75 | 0.44
14 | Prescott | 484 | 0.8 | 0.66
15 | Prescott | 484 | 0.45 | 0.6
16 | Prescott | 484 | * existing break in fiber
17 | Prescott | 484 | not terminated in Prescott
18 | Prescott | 484 | not terminated in Prescott
19 | Morison | 477 | 0.65 | 0.58
20 | Morison | 477 | 0.35 | 0.12
21 | Morison | 477 | 1 | 16.45 | FAIL
22 | Morison | 477 | 0.55 | 16.6 | FAIL
23 | Turner | 315 | 0.15 | 16.86 | FAIL
24 | Turner | 315 | 0.6 | 15.66 | FAIL
25 | Turner | 315 | 0.6 | 0.21
26 | Turner | 315 | 0.25 | 0.38
27 | Parrington | 344 | 0.7 | 0.44
28 | Parrington | 344 | 0.75 | 0.43
29 | Parrington | 344 | 0.9 | 0.79
30 | Parrington | 344 | 0.65 | 0.38
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144