Cable Plant Week of February 27, 2004

Russ’ Projects:

The summary of my week’s activities are:

Met with the Architect to assist with renovation design for Kresge R7

The installation of the additional telco cable between coll. 9 ADF and the student Health Center had the pull rope installed. The run looks fairly easy. I am also writing the project specification documents.

Reviewed after project drawings for the Baskin Alterations project. This is the 1st I’ve heard of this project. The campus project manager did not have me review documents prior to the project.

Working with PP&C to finalize Shackell’s work in the FDM project. Latest item of concern is the cabling ‘j’ hooks falling from the ceiling due to improper tie wire used for installation.

Continued working with SBC regarding cable removal to support the Porter in-fill Apts. Some of the active circuits that need to be removed from the cables belong to UCSC. I will ID these circuits and work with Andy/Matt to relocate them.

At FSH, a recently installed telco cable splice case flooded, taking the cable out. I verified the problem and Neil coordinated the repair (warranty).

Reviewing the fiber to the desk top standard for new construction.  I am contacting the other campuses to see what they are doing with cabling, now and future. I also contacted two cable suppliers to visit with information regarding CAT6 cable.

Planning and packing for the move to the trailer. A P.O. is written to re-cable the trailer.

Reviewing construction documents for the following projects:

Humanities, 100% construction

ERC 50% construction

SBC CAMFAC cable install:

Coordinating activities between SBC and Jim Gabrio to get the conduit installed.

SBC will saw cut the concrete into the above ground splice can. CAMFAC will dig the trench and install the conduit. I am obtaining a schedule from CAMFAC to coordinate the efforts.

CAMPAC has installed a 50pair cable into the SBC above ground splice can and wants it removed. I am working with SBC and CAMFAC to find a solution as the cable is important. I met with Gabrio, who is willing to install a new 2” PVC conduit between the MH and SBC’s splice can at their expense. The cable CAMFAC installed is the main substation control cable and is VERY important. I have passed on Gabrio’s offer to SBC and am awaiting their comment.

Thimann 191 / Lick Expansion:

After a flurry of email regarding our policy of extending fiber and creating new single use IDF’s, we still have not reached a resolution to present to Lick. I will attempt to gather a consensus next week.

Kerr 2nd Floor Renovation:

Worked with Staff Human Resources regarding relocating their computer training lab from the 2nd to 1st floors. This includes sizing and locating a new telcom closet that will feed the entire floor.

I finalized a preliminary budget and met with the project manager to review the budget.

East Field House to OPERS cable replacement:

Reviewing pathways and sizing cable to determine method of replacement.

Mary’s report:

Project listing 02/26/04

- Assigned self-reporting division network updates for Pinnacle, by Rich.

  - Ed has assigned David Hayden to the network side of Pinnacle.  I will pass this on to him.  Bob says this can only be accomplished after the Pinnacle conversion.  Marcy stated that Michael told her, his techs had all the correct information for importing.

  - 1/29 So, do I pass this off to David?

  - 2/19 I suggest this would be a wonderful project for the Telcom CSRs to learn the networking side of Pinnacle.

  - 2/26 No change

  - 3/04/04 Still waiting for direction on this project.

- Investigating setting up Pinnacle to better track data needed for the small wiring projects.  The new database is very complex, documentation is vague, therefore reading and experimentation in the test database is necessary to accomplish this task.  Implemented a process in the test database for Marcy & Neil to test.

  - Will schedule meeting with Marcy to assess where she is at in testing of new procedure.

  - 1/21 sent email enquery

  - 1/29 Marcy will get back to me, when billing is done and she has time.

  - 2/19 no change

  - 2/26 sent Bob and Marcy email asking how they want to finalize this project.  Did they want input, or should I just configure and implement.

  - 3/4/04 Marcy was to set up meeting for items 2 and 3, with David, she and I, this week.  However, she was ill and unable to do so.  She will schedule next week.

- Bob has asked that I assist in moving MAC template creation forward as it is the key to the Pinnacle web access.

This item was assigned to David Hayden, by Ed Titus, during the Pinnacle Web kick-off meeting.

1/21 – I spoke with Jim of Pinnacle, at length regarding MAC templates and the new web interface, and how data still doesn’t work well with the latest version of Pinnacle.  I brought up voice over IP as an example of true integration of data and voice.  If they can’t get Pinnacle to work well with data now, voice over IP isn’t going to fit, either.  He agreed the web interface was very poor, and assured us, the next rewrite has completely changed the face of Pinnacle and will be far superior.  In the mean time, we’re stuck with “monkey” rigging the MAC templates for data use.  He gave me a few good suggestions at using tasks and services.  I could throw something together on the test database and see how that works.  Until Pinnacle gets it’s customer base together…..I’d like to investigate ColdFusion, to see if it can provide temporary solutions for the data side of the database.

  - I ordered “ColdFusion MX Web Application Construction”, should arrive this week.  I paid for this item, myself, as I preferred to maintain ownership of the item.

  - Do you still want me to work at creating MAC templates for data, or, should Marcy and David be interfacing to complete this task?

  - 1/29 Any answer to about question?  Until I otherwise, I am going forward on templates trials and errors.

  - 1/29 Received book, installed the 30 day demo version of ColdFusion MX on my machine.  Book is an extremely detailed tutorial, I’m in Heaven!

  - 2/19 no change, Infill and Eng building became top priority for this week.

  - 2/26 sent Bob and Marcy email asking how they want to finalize MAC web template project.  Did they want input, or should I just configure and implement.  Meanwhile, have been learning ColdFusion when time allows.

  - See item 2.  And, I’m still knee deep in ColdFusion lessons.

- Correcting and update of NTS web site.

        - Updating and correcting when notified.

        - Need guidance on reconciling “hourly charges” with “consulting services” rates.  They are very different, need to know which numbers to use for “hourly charges.  I suggest the “consulting” rates.

-12/11 Still no word on this.

-12/18 Still no word on this.

-01/08 Still no word on this

-01/21 Still no word….

-01/29 Ditto

-02/19 Ditto

-02/26 Ditto

-03/04/04 I’m dropping item B.  I will continue to update NTS web site when notified.

- Proposed inventory plan for waps installation.  Accepted by Rich and Frank (per Rich).  Test bed likely to be installations in Col 9/10.

  - 12/11 Objections from Frank, sent off my response, haven’t heard back from anyone.

  - 12/18 Have had no notification or communication on this item from other parties involved.  Had expected this to be an item of discussion at the weekly wireless meeting, but it was never raised.

  - No change

  - 1/21 Have received email from one Mr. Koch’s students, Paul, stating that Mr. Koch has assigned this task to him, and I’m to assist.  The cut sheet provided did not have enough information to properly inventory the wireless network into Pinnacle as per the outline approved by Mr. Chew.  I would be happy to assist when the required information is provided.

  - 1/29 No change other than a questioning email from Mr. Koch.

  - 2/19 Ditto

  - 2/26 Haven’t heard back from anyone…

  - 3/4/04 Ditto

- Working on numbering.

  - PSB  Met with Glen Mah on PSB regarding floor changes.  Drawings are so messed up; he will obtain drawings from wiring contractor to provide accurate cabling installation.  May require complete renumbering.

- on hold for Glen, no change

-Heard from Glenn, he says,

“Mary -  I don't have any good news for you.  The project continues to fall behind schedule and we have some hard decisions to make this month.  Regarding the comprehensive telecom drawings I asked the subcontractor for ... I was told that since the project has been delayed so long, Pacific Com Tel is refusing to do the work, so they aren't doing any shop drawings either.

If you are continuing to have difficulty reading the design drawings (as I am also) due to changes and inconsistencies on the telecom ... contact Richard Spiese at 415-946-0273 who did the design.  He should be able to help you with those symbols, etc.”

I will contact Mr. Spiese, next week.

1/21 Haven’t contacted Mr. Spiese, am working on Eng. Bldg jack numbering.  I’ll call him sometime Thursday or Friday.

1/29 No change

-2/19 Glenn meeting with contractors, Russ to attend.

-2/26 No change

-3/4/04 Sent Vicki McCarroll, Rich McMillian and Glenn Mah email.

Told Vicki and Rich, I would have to redo jack numbers and asked

Glenn to get me some new drawings as soon as possible.

  - Infill is done and handed off to Kevin.

  - Engineering – had questions, Bret will get back to me with the answers.

Still waiting on Bret, he’s waiting for new drawings.

    - Will email Bret for an update

    - 1/21 working on jack numbering. Only half through 2nd floor and already have 571 CAT5e and 59 fiber.

    - 1/29 Still working on Eng. numbering, 1/3 through 3rd flr, up to 1527 CAT5e and 190 fiber.

    - Done….3824 copper and 642 fiber

    - 2/26 Need to burn CD and send to project manager

    - 3/4/04 Burning CD…..today!

- Working on new cable numbering for infill and new buildings.

PSB – done, need inventorying  - no change

Infill – 3/4/04 Done, will pass on to Kevin

Engineering – Done, will pass on to Bret.

- Still no word as to when the fiber inventory project will be given any priority and reassigned a technician.

-There have been data/voice cable inventory projects; at the moment Mike has Joe inventorying jacks against the database.  Why is the fiber inventory project consistently being ignored?

  - Since there’s NEVER any change in the status of this project, shall I just drop it from my queue?

  - 12/11 no change

  - 12/18 no change

  - 01/08 no change

  - 01/21 no change

  - 01/29 no change

  - 02/19 no change

  - 2/26 Ditto

  - 3/04/04 Ditto

- Notified Russ and Neil for draft updates of Cable management web pages.  Preliminary date is Nov. 15th.

  - No change.  Haven’t received any updates.

  - Will check with Neil on status.

  - 1/21 Neil to work on it after vacation

  - 1/29 Expecting preliminary draft by 2/9

  - 2/19 was out sick the 9th.  Neil working on this, need prelim date is 3/1

  - 2/26 no change

  - 3/04/04 Ditto

- Cleaning up tiff drawing of FSH.  Plan is to turn this into a CAD drawing when the tiff is cleaned up enough to follow as a guide.  Just something I’m trying my hand at.

  - Since this is not a high priority item, I work on it, intermittently.

  - No change

  - Almost finished…….

  - No change

  - No change

  - No change

  - Low priority, but, still 96% done

- FYI, Media services are interested in accessing Pinnacle for their needs.  They’ll schedule some time when they are available.

  - 3/04/04 Will keep this on my list to remember to check in with Media Services once in awhile.

- Marcy has brought up the issue of changing room numbers.  FDX, the asset  managers, will renumber rooms to meet their specifications.  This doesn’t always get communicated to all units that require that information to be accurate.  I see this as an issue that is best resolved with technology and not massive data entry.  The Pinnacle database should be tracking FDX database as a source for this accurate information, monthly.  Databases utilized and/or created prior to our purchase of Pinnacle, were set up to utilized FDX as the master source.  I feel this is a good example of IT consolidation…

  - 3/04/04 Don’t see this as an action item, just a FYI.

- Tad requested new coverage map of the wireless project, indicating what building had active wireless coverage.  Working on this, as he needs it by Monday, 2/23.

-Vic offered his map, which showed coverage, already.  By 4:30pm, Friday, I had not heard back from Tad as to what he wanted.  Had printed out Vic’s map, but no one picked it up.  I was out sick Monday & Tuesday.

-3/04/04 Via email from Vic, Tad wanted 4 printed out before lunch, today.  Vic will stop by and pick up.

14.  Planning to pack up, next week, 8th through 12th, for out move on the 18th.

Neil’s projects:

Small Cable Projects:
NW 251 - 1 FiSH. Add 3 data Jacks to new office in residence area - Waiting for customer. Now 90 days old.
 NW 254 - 1 Comm Bldg. Did contractor walkthrough.  Cyclops to bid. Received and forwarded bid.
NW 255 - 1 Kresge. Did contractor walkthrough.  Cyclops to bid. Received and forwarded bid.
NW 256 - 1 Stevenson Acad. Did contractor walkthrough.  Cyclops to bid. Received and forwarded bid.
NW 257 - 1 Hahn. Work to begin week of 3/8/04.
NW 258 - 1 Hahn.  Did contractor walkthrough. Bid expected week of 3/8/04.
NW 259 - 1 Thimann lecture hall.  Did contractor walkthrough.  Bid expected week of 3/8/04.
NW 260-1 College Dining Halls project. Did walkthrough with Lindsay. Assembling bid documents.
NW 260-2 College Dining Halls project. Did walkthrough with Lindsay. Assembling bid documents.
NW 260-3 College Dining Halls project. Did walkthrough with Lindsay. Assembling bid documents.
NW 260-4 College Dining Halls project. Did walkthrough with Lindsay. Assembling bid documents.
NW 260-5 College Dining Halls project. Did walkthrough with Lindsay. Assembling bid documents.
NW 250-6 College Dining Halls project. Did walkthrough with Lindsay. Assembling bid documents.
NW ?        Cable Plant Trailer: Did contractor walkthrough.   Bid expected by 3/10/04.


Capital projects: See attached Capital Project Report.

IMPORTANT NOTES ON CAPITAL PROJECTS:

        The Engineering Building will be completed on May 31, 2004 and "handed over" to UCSC on June 1, 2004.
        The Stevenson Infill project will be completed on May 31, 2004 and "handed over" to UCSC on June 1, 2004.
        The Cowell Infill project will be completed on May 31, 2004 and "handed over" to UCSC on June 1, 2004.
        The Porter Infill project will be completed on May 31, 2004 and "handed over" to UCSC on June 1, 2004.

Engineering Building:

03/04/05

The Engineering Building will be completed on May 31, 2004 and "handed over" to UCSC on June 1, 2004. Rough-in cabling has been completed on the 3rd, 4th, 5th floors and is underway on the 1st and 2nd floors.

02/26/04

Rough-in cabling continues at a rapid pace.  No terminations at this time.

02/12/04

The Engineering building is approximately four months ahead of schedule..

Rough-in cabling has been completed on the fifth floor of the Engineering Building.

Rough-in cabling is approximately 75% completed on the fourth floor.

Rough-in cabling is approximately 33%% completed on the third floor.

02/05/2004

Cabling has begun on the fifth floor of the Engineering Building

1/15/04

Began inspections of Eng. Bldg.  Kelly Stevenson, PP&C inspector and I toured the entire project, inspecting the five floors.  Work on the upper floors is more advanced than on the lower floors. The building is still on temporary power.

Rosendin electric will be the sub for electrical and data work.  Having the same company perform both functions will eliminate a lot of finger pointing during the project.

Cable tray and conduit have been installed throughout the building.  Grounding and bonding has begun on the cable trays.  The conduits that feed workstations have not yet been bonded to the tray. The 4” conduits that carry cabling through the hard-cap sections of the building have been installed, and look good except for a section on the 3rd floor south section, The one problem section was moved by the sprinkler installers, and will need to be realigned with the cable trays on both ends.

The conduits and gang boxes for workstation cabling have been installed.

The cable trays are rapidly being obscured by the mechanical work and sections of suspended ceiling.  Cable installation will be much more difficult than it would have been a month ago.

Data and voice cabling are scheduled to begin within the next few weeks.  This work will be done concurrently with the electrical work.  Communications cabling is slated to be completed within six weeks of commencement. Due to the large number of connections and the increasingly tight conditions, this will require a large installation team, possibly one team per floor.

Fire alarm cabling has begun on the fourth floor.

In general the project is going very well, and looks to be completed earlier (May or June 2004)

than the scheduled completion date.

PSB Report:

03/04/04

No change from 02/26/04.

02/26/04

Pacific Comtel has resurrected their contractors license which is now “Active”. They will be re-bidding the project with Hubbell/Commscope materials instead of Panduit/Berktek products.

There is only a skeleton crew working on the building.  This prevents UCSC from stating that the contractor has abandoned the project, but little real progress is being made.

02/12/04

There is no progress to report on PSB. The project is about one year behind schedule. Pacific Comtel’s license remains suspended.

02-05-04

Atkins construction has won a judgment against “Commerce Air”, the mechanical contractor whose license was suspended by the Contractors State License Board.  Atkins will begin moving equipment and materials out of Commerce’s shop to the PSB job site.  The lack of these materials has caused delays for the last six weeks.  This should allow for progress at PSB.

Pacific Comtel’s license remains suspended.  They are not only without bond, but are now lacking a qualifier.

1/29/04

Pacific ComTel has been working on an updated bid for the project.  Unfortunately, Pacific ComTel’s license has been suspended by the Contractor’s State License Board, and they may not legally bid on, or perform on any contractor work.  Legal maneuvering has begun on the project, and the project itself is clearly in jeopardy.  Tim Basquez feels that the situation may be clearer after the first week of February 2004.

1/15/04

One additional stick of cable tray has been added to second floor. Several existing cable trays have now be bonded together and to conduits for grounding purposes. There are only a few workers on each floor. The project is severely delayed and has major problems.

---------------------------------

1/08/04

The general contractor has taken over the role of Mechanical Contractor at PSB.  The current workforce at PSB is 50 workers - about 50% of the proper staffing.  That number will fall to about 25 workers as the subcontractors continue to lay off or reassign workers.  UCSC is looking into the possibility of legal action concerning the project.  During the last subcontractors meeting, Pacific ComTel announced that they would not be working on the project.

If the project gets back on track, the earliest expected completion date is early in 2005.

--------------------------

PSB has had no reportable progress since the last report.

Due to holdups concerning the bankruptcy of the mechanical contractor and the delays to the trades that follow his work (sheetrock, tape/texture, paint, ceiling grid) the cable trays will not be installed for about two more months.  The cabling work will not begin until the trays have been completed on the first and second floors.

At the same time, Pacific ComTel has indicated that they no longer want to perform on the project for the agreed price.  Due to the amount of time that has passed since the contract was signed, they do have that right.  There will be a meeting this week between Pacific ComTel and Helix to help determine the future of Pacific Comtel at the PSB project.

The new (unofficial) completion date for the project is November/December 2004.

The official completion date was listed as November 2, 2003.  The contractor's schedule shows final completion at 12/1/03.  The most likely actual completion date (unofficially) is now Summer 2004.

- It appears that cabling will not commence in late October or early November.  Kelly Stevenson indicates that the 4" telecom conduits are properly supported.  Cabling may start in November or December.

-The T rating of both the electrical closets and data closets have been causing delays. The electrical closets have been combined into a “shaft’ between all floors.

-The activity of starting the telecomm room on each of the floors, which was listed for August 11th, is scheduled for this week.

- More cable tray has been installed, but is not completed.  Some cable tray has been removed to allow other utilities to pass at right angles and at the same height as the tray.  This is going to cause complications for the cabling crew unless corrected.

-The roofing is not completed and the membrane is damaged in several locations.  If it rains, there will be a problem.

1st Floor:

Data closet on the first floor is sheet rocked and taped.

There is still no cable tray on the first floor.

Sheet-rocking and taping is ongoing on the entire floor

The main cable conduits are only a few inches above the door in the data closet.  We will need to check the height of the cable tray on the elevation plans.

2nd Floor

The data closet on the second floor is rocked, but not taped.

Most cable tray is installed and grounded.  The cable tray has been routed over an air handler – cable installation will be harder than it should be.

T-Bar ceiling is installed in many locations.

3rd Floor

Data closet is 40% rocked, not taped.

Cable tray by closet (Drawing notes #1) is installed but not grounded.  The clearance between the cable tray and ceiling will be very tight (less than 8”). No other tray has been installed since last report.

Sheet-rocking and taping is ongoing on the entire floor.

T-Bar ceiling is installed in many locations.

Referring to drawing notes 7&8: Conduit and tray are installed without ground wire.

4th Floor

Data closet <50% rocked.

Referring to drawing note 8 on second page: Conduit and ground wire installed – no tray.

Note 1: Tray and ground wire installed.

Note 2: Conduit is installed.

Note 5&6: Tray still not installed

Sheet-rocking and taping is ongoing on the entire floor.

T-Bar ceiling is installed in many locations.

5th Floor

Note 3: 1 stick of tray installed. No ground wire.

Steel 2x4’s installed for hard-cap ceiling.

Roof

A roofing contractor is on-site.

-------------------------------------------------------------------------------------------------------------------------

Film and Digital Media Remodel

03/04/04

Jacks on the 1st floor of  F&DM have been renumbered by Network Ops staff. Existing plans and the contractor’s as-built drawings will now be incorrect.  A problem was found with the wires supporting J-hooks.  Too fine a gauge of wire was used, and will need to be replaced throughout the entire building.

We have received certifications for all inside cabling at F&DM with the exception of jacks 055 – 066 in room 11.  Voice and data cabling to the telecom trailer has not been completed.

02/26/04

Shackell has completed the voice cross-connect system on the ground floor.  Certifications have not yet been received.  Shackell has installed an 18-strand hybrid fiber cable and coiled it and the telephone backbone cable near the Telco trailer.  Shackell will install the cables in concert with the new conduit being placed by Adacon (possibly by Feb. 27, 2004).

Defective MT-RJ connectors have not yet been replaced.  All certifications that were outstanding in the 02/19/2004 report are still outstanding.

02/19/04

Shackell has received most materials to completed project.  We will be supplying Shackell with 8MM/4SM fiber for trailer.  Jack nearest main floor bathrooms still needs to be moved. Certifications for Room 11 reterminated jacks are still outstanding.

02/12/04

Shackell has adopted the fiber testing method that I supplied to them.  This method allows them to meet TIA 568B test specifications.  Results on all but 12 cables are now acceptable.  Shackell is ordering additional MT-RJ connectors to complete the work.

Shackell is ordering substitute materials for the RJ-21x cross-connect system for the ground floor.  Pre-connectorized Cat3 components are becoming harder to find, so a contractor-built product will be substituted.

The backbone copper cable to the telecom trailer has not been installed.  Installation will take place after Adacon moves out of the adjacent trailer.

We have not yet received certifications for the cables in room 11 that Shackell needed to reterminate.

02/04/2004

Much of the main floor copper has been reterminated and recertified.  Fiber cables have not yet been reterminated or retested.  The RJ-21x cross connect system for voice feed to the ground floor has not been started.  Nine cables on the ground floor still need to be reterminated and recertified.  The replacement CATV cable has not yet been installed.

The HVAC system continues to be a problem, and Adacon’s decision to waive the pre-inspection report of the HVAC system has made them responsible for some of the older existing problems with the system, including many clogged heat coils.  Due to the above problems, the HVAC system cannot be balanced at the current time. This is delaying the final inspection by Chief Hernandes.

1/29/04

There continue to be major problems with both progress and quality of work at F&DM.  We have received a second set of fiber test results which are not acceptable due to high loss on some fibers, and high ‘light-gain’ on others. Today’s meeting with Shackell and Adacon will be used to review results, testing methods and to arrange for witnessed testing of the fiber.  I have supplied Shackell with specifications detailing how to test MT-RJ connectors with their cable tester.

The voice cross-connect cables for the ground floor have not been started.

Shackell has reterminated the worst of the copper cables on the main floor, and supplied certifications for that work.

Fiber labeling has been completed on the main floor.

Much of the PVC cable has been removed from the cable trays on the first floor.

Fiber and copper to the telecom trailer has not been completed.

1/15/04

Shackell has two employees on site.  They are in the process of reterminating the failed fiber connectors.  They are planning to complete the RJ-21x cross connect system on the ground floor by 1/23/04.

The F&DM meeting was cancelled by the contractor this week.

Cabling Punchlist items continue to increase faster than they are being resolved.  The lack of the RJ-21X cross connect system on the ground floor prevents activation of voice services on new cabling on this floor.  Much PVC cable remains in the cable trays.  Shackell Telecom has not increase manpower to meet the needs of the project.  The termination and testing of MT-RJ connectors continues to cause difficulties for Shackell.

Adacon has begun moving out of their trailer and plans to have the trailer painted and carpeted by Feb 2, 2004.

-----------------------

There are a number of issues with the F&DM project.  Almost all fiber cables have failed certification.  The copper cables in the main floor closet need to be reterminated.  Cabling to the trailer has not yet been completed.  Many punchlist items remain.

-----------------------------------

Punchlist is attached as a separate file. Punchlist items are being forwarded to Kevin as they are found.

Family Student Housing (Repair and Broadband)

03/04/04

The copper splice case installed by Shackell has failed. The cables have been re-spliced and a new gel-filled case installed.  New copper tests are now required from Shackell.

02/19/04  We have received and accepted the copper test results from Shackell.

02/12/2004  We still have not received the final documentation from Shackell on this project

02/05/2004  We still have not received the final documentation from Shackell on this project.

01/29/04

I have supplied Shackell with yet another copper test form.  We hope to receive the copper test results this week.  We have received the fiber results which I have yet to review.

1/14/04

We still have not received test results from Shackell telecom.  Repeated requests have not helped.

----------------------------------

We still have not received results for copper backbone testing for this project. We are still waiting for SM results for Porter to FSH.  Bruce Hoffmann is aware of the lack of results.

---------------------------------

Shackell is scheduled to complete work on FSH on 12/5/2003.  Work completed on 12/12/03.  Need to check certifications supplied. Still waiting for SM results for Porter to FSH.

This project has occupied much time in the past two weeks.  Working with both Bruce Hoffmann and Courtney Grazian.  Fiber test results are attached as a separate document.

Infill Projects:

The Stevenson, Cowell, and Porter Infill project will be completed on May 31, 2004 and "handed over" to UCSC on June 1, 2004.

Porter Infill Report:

03/04/04

Porter Infill progresses rapidly. Work in telecom closets in Building 72, 74, and 75 is underway.

02/26/04

I have layed out the telecom closets in Buildings 72, 74 and 75. Termination in these closets has begun.  Station cabling is mostly completed in these buildings, but I have not yet checked jack numbering.

2/11/04

Termination of jacks has begun in buildings 74 and 75.

1/29/04

TMX is concentrating most of their effort in Stevenson, but once Stevenson and Cowell are completed, work should advance rapidly on this project.

1/15/04

Building 71: Sheetrock almost completed. No tape and texture. Building exterior being finished.  All cable roughed-in. Cables are not yet numbered.

Building 72. : Sheetrock almost completed. Tape and texture completed.  Building is painted.  All cable roughed-in. Cables are not yet numbered.

Building 73. No access due to painting.

Building 74. Sheetrock completed. Painting 90% completed. Cabinetry not installed. All cable roughed-in. Cables are not yet numbered.

Building 75. Sheetrock completed. Painting completed. Cabinetry installed. All cable roughed-in. Cables are not yet numbered.  Outer doors installed.

Building 76. No access due to floor surfacing.

Building 77. Least advanced building.  Interior walls being installed. Cables roughed-in. Cables are not yet numbered.

---------------------------------------------

There has been little reportable progress on the cabling at this project.

___________

The rough-in cabling in all of the Porter Infill buildings 71, 72, 73, 74, 75, 76, 77 has been completed. All but building 77 are sheetrocked.  Many are taped, textured and painted.

The voice and data work has not be started in the closets and no station jacks have been installed.

Devcon reports that 90% of communications/CATV work is completed.

Porter Infill is composed of buildings 71, 72, 73, 74, 75, 76, 77.

Building 71 is in the framing stage and utilities have not yet been installed.

Building 72 has all voice/data/catv cabling roughed-in.

Building 73 has been rocked, but no voice/data/CATV is visible)

Building 74 has all voice/data/catv cabling roughed-in.

Building 75 has all voice/data/catv cabling roughed-in.

Building 76 has some rock but utilities have not yet been installed.

Building 77 is in the framing stage and utilities have not yet been installed.

Stevenson infill Report:

03/4/04

Continuing inspection of project. Backbone terminations are still in progress.  All other cabling work is nearing completion.  Terminations have not yet begun in ADF3.

02/26/04

Continuing inspection of project. Backbone terminations are in progress.

2/19/04

Continued inspection of project.  Helped expedite order for elevator phone.

2/11/04

There is great progress at the Stevenson Infill project.   Building 43 has all jacks installed and labeled. All labeling agrees with the construction documents.  Certifications have not been received.

Building 41 has almost all jacks terminated.  I have begun comparing actual jack numbers to the construction documents for accuracy.

02/05/2004

Building 43 data closet:  Data jacks 905-001 through 905-110 are terminated in order and neatly labeled. Voice jacks 905-001 through 905-095 are terminated to 110-blocks in order and are neatly labeled. The 100-pair voice backbone is terminated to 110-blocks but not labeled.

Fiber and CATV are coiled in room.

Building 43 Units A, B, C all floors:  Wall plates are installed.  Data and voice jack numbering conforms to plans.

Building 42 closet has data station cables coiled above the data rack.  None are terminated,

The 100-pair voice backbone is terminated to 110-blocks, but not labeled.

Voice station cables are terminated to 110-blocks, but not labeled.

The CATV and fiber cables are coiled in the room.

01/29/04

Installation of wall-plates and final jack numbering has begun in building 43.  The project continues to look very good, and hand-over of the buildings may happen as soon as May 2004.

TMS requests for change order payment has been declined.  The work on Stevenson Infill goes very well.  Stevenson Closet 41(A) cables 906-D001 through 906-D200, as are 906-D209,210,300,301, 302, 400,401 are terminated and labeled.

Voice station cables are terminated and labeled. There are skips in the numbers: V301,302,401 through 409.

Backbone cables (fiber, copper, CATV) are run and coiled in room but not terminated.

Almost all workstation jacks have been installed.  The jacks checked for numbering accuracy (about 50% at this time) are all good.

There is still no access to the closet in Bldg 42.

The closet for bldg 43 has voice cables 905-V001 through V095 terminated and labeled.  Data cables are terminated but not labeled.

Backbone cables are coiled in 43 but not terminated.

----------------------------------

There has been a lot of progress in the Stevenson Infill project.

Building 41: The contractor has completed voice station cable termination in the equipment room.  The work looks clean.  The backbone voice cable has not yet been terminated.  The fiber has not yet been terminated.

The data rack has been installed and the contractor is dressing the cables.  No data cables have been terminated to the rack yet.

All of the station cabling has been roughed-in except for the computer lab which has not yet been cabled.  No data or voice station jacks have been installed.

Building 42:  All of the station cabling has been roughed-in. The contractor has completed voice station cable termination in the equipment room. The backbone voice cable has not yet been terminated.  The fiber has not yet been terminated.

The data rack has been installed and the contractor has begun dressing the cables.  No data cables have been terminated to the rack yet.

No data or voice station jacks have been installed.

Building 43 (Units A-E): All of the station cabling has been roughed-in. The contractor has completed voice station cable termination in the equipment room. The backbone voice cable has not yet been terminated.

The data rack has been installed and the contractor has dressed the cables.  Data cables are terminated to the rack

All voice and data station cables have been terminated.

Devcon reports that 90% of communications/CATV work is completed.

Buildings 41A , 41B have Cat5E cabling to all residence rooms.  Cabling is run back to one closet in building 41B.  No cables are terminated.  One cable in 41A lower floor is damaged in the cut-in box, but TMX should be able to terminate it - the short length may cause problems removing the cover plate.

Buildings 42 and 43 have Cat5E cabling to all residence rooms.  No cables have been terminated.

Cowell infill Report:

03/04/04

Laying out closets for Cowell B11 and B12.

02/26/04

No changes since last report.  TMX is working on closets at Porter and backbone at Stevenson.

2/19/04

TMX is concentrating most of their effort on Cowell. Cable termination continues.   Termination in closets will begin 4/23/04.

02/11/04

Cowell  has seen little cabling progress this week.  Most of TMS effort is centered on Stevenson and Porter. When painting is completed at Cowell we should expect to see more rapid progress.

02/05/2004

No changes to report.

01/29/04

Cowell  has seen little cabling progress this week.  Most of TMS effort is centered on Stevenson. When painting is completed at Cowell we should expect to see more rapid progress.

01/15/04

No walkthrough this week.

----------------------------------------------

01/08/04

There has been little reportable change in the project.

-----------------------------

Building 13A (Community Room) is being framed.  No cabling work as yet.

Building 13 (Dorm): All of the station cabling has been roughed-in.

Building 12 (Lower): All of the station cabling has been roughed-in.

Building 12 (Upper): All of the station cabling has been roughed-in.

Building 11 (Lower): All of the station cabling has been roughed-in.

Building 11 (Upper): Most of the station cabling has been roughed-in.

Closet work has not yet begun at the Cowell Infill buildings.

Cowell Infill is composed of buildings 11, 12, 13 and 13A.

Devcon Construction reports that 65% of communications/CATV work is completed.

Building 11 is being framed.

Building 12 has cabling in the 1st to 2nd floor apartments but not the 2nd to 3rd floor apartments.

Building 13 has roughed in cabling in almost all sections.